HVAC Design From Clean Sheet to Blueprint – A Mechanical Designer’s Guide to Design of Small Commercial and Institutional HVAC Systems

# Chapter 1 (Partial)

Procedure Outline – The Clean Sheet

## Scope

This book is not intended to teach engineering fundamentals, but to help trained mechanical engineers and technicians understand and undertake the HVAC design of small commercial and institutional buildings.  This chapter will outline the tasks that must be executed to arrive at a successful and cost-effective design.  Cost-effective from the standpoint of the project cost, but also from the standpoint of the design effort.  Clients for small building design, generally owners, architects, or contractors, have legitimate cost constraints, and designers who cannot work within those constraints will soon find themselves out of work.

## Important Terms

The following terms will be used throughout this book. They have specific meanings in connection with HVAC systems, ventilation, and indoor air quality.

A building is a roofed and walled structure with controlled environment, built for human occupation and use.

The thermal envelope of a building is the primary insulation layer of the building where resistance to heat transfer is the greatest.

The pressure envelope is the primary air barrier of the building, which is sealed to provide the greatest resistance to air leakage.

A zone is a group of spaces within the thermal and pressure envelopes which are served by a single air handling system.

A sub-zone is a group of spaces within a zone that may be served by a single terminal component such as a variable air volume unit.

A space is a single room, with or without a ceiling plenum.

A room is the part of a space bounded by walls and a ceiling that is usually routinely occupied and served by grilles and registers to supply and recirculate or exhaust

1

conditioned air.

A ceiling plenum is a cavity within the pressure envelope that is above a room and that is formed by a dropped lay-in ceiling and floor or roof structure above. Room walls do not necessarily extend above the dropped ceiling to the structure above.

A return air plenum is a ceiling plenum with an unobstructed path to an air handler return, and that contains no flammable materials or surfaces.

Supply air is the all of the air delivered by the cooling/heating apparatus to the supply air diffusers in the zone.

Outdoor air, also called ventilation air, is air from outdoors that is mixed with return air before passing into the cooling apparatus.

Return air is the portion of the supply air that is recirculated after being collected by the return grilles in the zone.

Exhaust, or exhaust air, is the portion of the supply air that is discharged from the zone to outdoors after passing through the zone.

In general, the thermal and pressure envelopes must coincide. However, if they don’t, they must be arranged so that outdoor air cannot leak into the space within the thermal envelope – remembering that the thermal envelope generally offers no resistance to air leakage.

## Proceeding to the HVAC Blueprint, an Outline

The following outline follows the organization of the chapters in this book.

Gathering Information - This may be the most important part of the designer’s job. Chapter 2 discusses the types of information that are needed, what to look for, and the responsibilities of the HVAC designer to review the data supplied and point out problems that may adversely affect the HVAC design or the building operation.  The base sheet should be prepared (Chapter 11) as soon as the architect’s floor plan is received.

Preliminary Design – Decisions are made about the types of systems to be used, building zoning, equipment locations, and routing of ductwork.

Establishing the Building Air Balance – The requirements for exhaust air and outdoor supply air for each zone must be established prior to calculating cooling and heating loads to ensure that the building remains under positive pressure at all times when occupied, and positive or neutral when unoccupied. Commercial kitchens and

2