## Input
Ductwork System Calculation Input Data Sheet
This Excel Workbook with Visual Basic Macros is offered for free download AS IS without warranty. The author makes no representations or warranty, either expressed or implied, with respect to the software program, its accuracy, its quality, or its fitness for any particular purpose. Anyone who uses this Excel Workbook to size ductwork or estimate duct pressure losses is expected to be experienced in manual procedures for duct sizing, design, and estimating pressure loss and is not to rely solely on the results from this software. Therefore the Author shall have no liability to any user with respect to any liability, loss, or damage caused or alleged to have been caused either directly or indirectly by its use. This includes but is not limited to interruption of service, loss of data, loss of consulting or anticipatory profits, or consequential damages from the use of this software.
| System/Zone Name: | XYZ system |  | Project: | UVW-123456
| Designed by: | Designer |  | Date: | 2009-10-20
To run this program, fill in the input below, then go to sheet 1 and run the macro "friction factor". A further explanation of how this spreadsheet works is given on sheet 1. For guidance in selecting values for the input, consult the ASHRAE Handbook, Fundamentals, "Duct Design". This is Chapter 21 in the 2009 Handbook, but the chapter may be different in other editions. Data generated by sheets 1 and 2 will automatically be entered in the "Report" sheet.
| Roughness e = | 0.0003 | [ - ]
| Air Density rho = | 0.0763 | [lbm/ft3] |  | Specific Volume = | 13.106
| dp/100= | 0.09 | [inwc/100-ft] | (Target pressure drop per 100')
| Kinevisc = | 0.000163
| Supply Air (SA) = | 1600 | [CFM] | Instruction:
| Outdoor Air (OA) = | 150 | [CFM] | 1) | Input blue cells in Input Tab,
|  |  |  | 2) | Do not make entry in gray cells
| No. SA Segments = | 7 |  |  | these are calculated cells
| No. RA Segments = | 4 |  | 3) | Run Macro 1: "fraction factor" in
| Total Duct Segments = | 11 |  |  | Sheet 1 Tab,
|  |  |  | 4) | Print out Report in Report tab.
fiting library
fitting type, C, and dp input by user
code | Fittings | Fitting C | dp [inwc]
1 | fan out | 0.72
2 | el | 0.11
3 | tee thru | 0.04
4 | tee branch | 0.8
5 | fan in | 0.3 |  |  | OA |  | SA
6 | diffuser |  | 0.04
7 | ret grille |  | 0.03
to override automatic duct air flow reduction (see sheet 1 instructions), set override = 1
For round duct, input height = 0 |  |  | override | 0
| segment cfm | duc height | segment L | Fitting Codes, each segment
segment | cfm | in | ft
1 | 1600 | 14 | 10 | 1 | 2 | 2
2 | 1600 | 14 | 5 | 2 | 2 | 0 | 0
3 | 1025 | 12 | 2 | 3 |  |  | 0
4 | 860 | 12 | 7 | 3 |  |  | 0
5 | 530 | 10 | 8 | 3 |  |  | 0
6 | 330 | 10 | 9 | 3 | 2 |  | 0
7 | 185 | 0 | 16 | 6 | 2 |  | 0
8 | 185 | 0 | 16 | 7 | 2 |  | 0
9 | 330 | 10 | 18 | 3 | 2
10 | 530 | 10 | 6 | 3 |  |  | 0
11 | 1600 | 14 | 20 | 3 | 2 | 2 | 5
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
AHU

## Report
Duct System Pressure Drop Calculation Result
System - Zone |  |  | XYZ system
Project Number |  |  | UVW-123456
Designer |  |  | Designer
Date |  |  | 2009-10-20
System/Zone Name: |  |  | XYZ system |  |  |  | Designed by: | Designer |  |  | Date: | 2009-10-20
duct | airflow | height | width | dia | velocity | Re | length | duct dp | dp/100' | vel. dp | fix'tr dp | tot. dp
leg | Q | H | W | D | V | Re | L | dP_duct | dp/100' | dP_v | dP-fit | dP_tot
No. | [cfm] | [in] | [in] | [in] | [fpm] | [ - ] | [ft] | [in. w.g.] | [iw/100'] | [in. w.g.] | [in. w.g.] | [in. w.g.]
supply duct
1 | 1600 | 14 | 17 | 16.8447 | 1033.8667 | 135888.7656 | 10 | 0.0096776 | 0.096776 | 0.06777 | 0.063704 | 0.073382
2 | 1600 | 14 | 17 | 16.8447 | 1033.8667 | 135888.7656 | 5 | 0.0048388 | 0.096776 | 0.06777 | 0.014909 | 0.019748
3 | 1025 | 12 | 14 | 14.1585 | 937.4731 | 103704.7188 | 2 | 0.0019934 | 0.099668 | 0.055722 | 0.0022289 | 0.0042222
4 | 860 | 12 | 13 | 13.6509 | 846.1505 | 90393.2344 | 7 | 0.0060285 | 0.086121 | 0.045395 | 0.0018158 | 0.0078443
5 | 530 | 10 | 11 | 11.462 | 739.6556 | 66329.5 | 8 | 0.0066726 | 0.083408 | 0.034687 | 0.0013875 | 0.0080601
6 | 330 | 10 | 8 | 9.7624 | 634.8522 | 48305.1992 | 9 | 0.0069559 | 0.077288 | 0.025554 | 0.0038331 | 0.010789
7 | 185 | 0 | 0.01 | 8 | 529.9847 | 36293.3555 | 16 | 0.010154 | 0.063465 | 0.017809 | 0.041959 | 0.052113
return duct
8 | 167.6562 | 0 | 0.01 | 8 | 480.2986 | 32890.8516 | 16 | 0.0084996 | 0.053122 | 0.014626 | 0.031609 | 0.040108
9 | 299.0625 | 10 | 7 | 9.11 | 660.6915 | 46574.8672 | 18 | 0.016442 | 0.091347 | 0.027676 | 0.0041515 | 0.020594
10 | 480.3125 | 10 | 10 | 10.9317 | 736.9259 | 63080.8555 | 6 | 0.0052636 | 0.087727 | 0.034432 | 0.0013773 | 0.0066409
11 | 1450 | 14 | 16 | 16.3519 | 994.2679 | 127096.6094 | 20 | 0.018627 | 0.093133 | 0.062678 | 0.0351 | 0.053727
[8 empty] | 0.095153 |  |  | 0.20208 | 0.29723

## Friction Factor (Sheet1)
DUCT SIZE CALCULATION SPREADSHEET |  |  |  |  | Run macro "friction factor" | [20 empty] | 75293.0312
Project | UVW-123456 |  |  |  | system-zone |  | XYZ system |  |  | fitting library
|  | <-- input data from Input tab | [7 empty] | fitting type, C, and dp input by user
formulas: | [9 empty] | code | Fittings | Fitting C | dp [inwc]
Reynolds Number | Re = 8.56*D*V |  |  |  | fixed parameters (user input) |  |  |  |  | 1 | fan out | 0.72 | 0
| D=(1.3(a*b)^.625)/(a+b)^.25 | [5 empty] | Roughness e = | 0.0003 | [ - ] | 2 | el | 0.11 | 0
| V=Q/((Pi*D^2/4)/144) | [5 empty] | Air Density rho = | 0.0763 | [lbm/ft3] | 3 | tee thru | 0.04 | 0
[7 empty] | Target dp/100' = | 0.09 | [inwc/100-ft] | 4 | tee branch | 0.8 | 0
Colbrook | 1/f^.5 = -2*log(12*e/3.7/D+2.51/Re/f^.5) | [5 empty] | kinevisc = | 0.000163 |  | 5 | fan in | 0.3 | 0
| dp = (12*f*L*rho*(V/1097)^2)/D | [5 empty] | Zone air flow = | 1600 | [CFM] | 6 | diffuser | 0 | 0.04
[7 empty] | Zone outdoor air = | 150 | [CFM] | 7 | ret grille | 0 | 0.03
Fitting Loss | vdp = rho*(V/1097)^2 | [5 empty] | specific volume = | 13.106
fitdp = vdp*C or fitdp = dp from fixture library
Fill out the input sheet. Enter supply segment air flows as they appear on the drawing. Return air flow will be less than supply air flow by the amount of the outdoor air flow, proportioned to each return grille. The user should enter the return air flows based on the supply diffusers serving each grille. The program will automatically reduce the return air for each segment by the ratio (supply - outdoor air)/supply. After the input sheet is completed and the macro "friction factor" is run, the size of each duct segment that will give the exact desired pressure loss per 100 feet of duct length is calculated and shown on sheet 2. If a height is imput, the exact width corresponding to the height and hydraulic diameter is also given. If height is imput as zero, round duct will be assumed. There is no need for the user to reference sheet two except to verify results.
In the real world, there are no decimal fractions in duct diameters or the width of rectanglular ducts. Also, the objective is to calculate the external static pressure for a fan or air handler. Therefore, the user must run the macro "friction factor" on sheet 1. This macro rounds the diameter of round ducts, or the width of rectanglular ducts to the nearest inch. If the duct is rectangular, the macro recalculates the equivalent diamter to correspond to the new width. Velocity (V) and pressure loss per 100' (dp/100') is then recalculated for the new hydraulic or integer duct diameter (dia D). Duct friction loss for each segment is calculated and totaled (duct dp). Fitting loss (fitdp), based on loss coefficients or pressure losses from ASHRAE data and manufacturer's performance data, is calculated based on the fittings input from the sheet "Input". Finally, the external static pressure (systotdp) is calculated and totaled.
Note that the duct legs below include both the supply duct segments and the return duct segments.
branch count max = |  | 11 |  | This macro will clear the contents of all calculated cells before running a new calculation.
duct leg | airflow Q | height a | width b | dia D | V | Re | L | duct dp | dp/100' | vdp | fitdp | systotdp | fitting C or dp |  |  |  | count | f' | fact | fact1 | diff | dpfixa | dpfixb | dpfixc | dpfixd
| cfm | in | in | in | fpm |  | ft | iw | iw/100' | iw | iw | iw | coda | codb | codc | codd | [5 empty] | iw | iw | iw | iw
supply duct
1 | 1600 | 14 | 17 | 16.8447 | 1033.8667 | 135888.7656 | 10 | 0.0096776 | 0.096776 | 0.06777 | 0.063704 | 0.073382 | 1 | 2 | 2 |  | 12 | 0.018272 | 7.3978 | 7.3979 | -6.3419e-05 | 0.048795 | 0.0074547 | 0.0074547 | 0
2 | 1600 | 14 | 17 | 16.8447 | 1033.8667 | 135888.7656 | 5 | 0.0048388 | 0.096776 | 0.06777 | 0.014909 | 0.019748 | 2 | 2 | 0 | 0 | 12 | 0.018272 | 7.3978 | 7.3979 | -6.3419e-05 | 0.0074547 | 0.0074547 | 0 | 0
3 | 1025 | 12 | 14 | 14.1585 | 937.4731 | 103704.7188 | 2 | 0.0019934 | 0.099668 | 0.055722 | 0.0022289 | 0.0042222 | 3 |  |  | 0 | 11 | 0.019262 | 7.2052 | 7.2052 | -5.6744e-05 | 0.0022289 | 0 | 0 | 0
4 | 860 | 12 | 13 | 13.6509 | 846.1505 | 90393.2344 | 7 | 0.0060285 | 0.086121 | 0.045395 | 0.0018158 | 0.0078443 | 3 |  |  | 0 | 9 | 0.01973 | 7.1192 | 7.1193 | -9.7275e-05 | 0.0018158 | 0 | 0 | 0
5 | 530 | 10 | 11 | 11.462 | 739.6556 | 66329.5 | 8 | 0.0066726 | 0.083408 | 0.034687 | 0.0013875 | 0.0080601 | 3 |  |  | 0 | 11 | 0.020992 | 6.9019 | 6.9019 | 7.1049e-05 | 0.0013875 | 0 | 0 | 0
6 | 330 | 10 | 8 | 9.7624 | 634.8522 | 48305.1992 | 9 | 0.0069559 | 0.077288 | 0.025554 | 0.0038331 | 0.010789 | 3 | 2 |  | 0 | 12 | 0.022404 | 6.681 | 6.6809 | 7.391e-05 | 0.0010222 | 0.0028109 | 0 | 0
7 | 185 | 0 | 0.01 | 8 | 529.9847 | 36293.3555 | 16 | 0.010154 | 0.063465 | 0.017809 | 0.041959 | 0.052113 | 6 | 2 |  | 0 | 13 | 0.023758 | 6.4878 | 6.4878 | 4.8637e-05 | 0.04 | 0.001959 | 0 | 0
return duct
8 | 167.6562 | 0 | 0.01 | 8 | 480.2986 | 32890.8516 | 16 | 0.0084996 | 0.053122 | 0.014626 | 0.031609 | 0.040108 | 7 | 2 |  | 0 | 13 | 0.024213 | 6.4265 | 6.4264 | 5.2929e-05 | 0.03 | 0.0016089 | 0 | 0
9 | 299.0625 | 10 | 7 | 9.11 | 660.6915 | 46574.8672 | 18 | 0.016442 | 0.091347 | 0.027676 | 0.0041515 | 0.020594 | 3 | 2 |  |  | 12 | 0.022651 | 6.6445 | 6.6444 | 8.2016e-05 | 0.0011071 | 0.0030444 | 0 | 0
10 | 480.3125 | 10 | 10 | 10.9317 | 736.9259 | 63080.8555 | 6 | 0.0052636 | 0.087727 | 0.034432 | 0.0013773 | 0.0066409 | 3 |  |  | 0 | 11 | 0.021232 | 6.8628 | 6.8627 | 8.8215e-05 | 0.0013773 | 0 | 0 | 0
11 | 1450 | 14 | 16 | 16.3519 | 994.2679 | 127096.6094 | 20 | 0.018627 | 0.093133 | 0.062678 | 0.0351 | 0.053727 | 3 | 2 | 2 | 5 | 12 | 0.018491 | 7.3539 | 7.354 | -5.4359e-05 | 0.0025071 | 0.0068946 | 0.0068946 | 0.018804
[8 empty] | 0.095153 |  |  | 0.20208 | 0.29723

## New Duct Size (Sheet 2)
Project
System-Zone |  |  |  | green cell: input data from Input sheet
calculation date |  |  |  | shaded cell: calculated by UDF or formula - do not make entry
Duct Size and Rectangular/round duct conversion
| supply air flow = | 1600 | cfm |  | dp100 = | 0.09
| outdoor air flow = | 150 | oacfm |  | e = | 0.0003
| return air flow = | 1450 | rcfm |  | rho = | 0.0763 | spvol= | 13.106
[5 empty] | kinevisc = | 0.000163
subcountmax = |  | 7 | supply duct segments |  |  |  |  | return segments = |  | 4
D=(1.3(a*b)^.625)/(a+b)^.25 |  |  |  | Curve fit of dia for dp100=.095 (first guess): |  |  |  | D=alog(.38352*log(cfm) + .00864)
airflow | height | dia | width | dp100 | L
cfm | in | in | in | iw/100' | ft
1600 | 14 | #VALUE! | #VALUE! | #VALUE! | 10
1600 | 14 | #VALUE! | #VALUE! | #VALUE! | 5 |  |  |  | module 1 |  | friction factor macro
1025 | 12 | #VALUE! | #VALUE! | #VALUE! | 2 |  |  |  | module 111 |  | fcalc | UDF
860 | 12 | #VALUE! | #VALUE! | #VALUE! | 7 |  |  |  | module 12 |  | AirCap | UDF
530 | 10 | #VALUE! | #VALUE! | #VALUE! | 8 |  |  |  | module 21 |  | Air Dia | UDF
330 | 10 | #VALUE! | #VALUE! | #VALUE! | 9 |  |  |  | module 31 |  | Wcalc | UDF
185 | 0 | #VALUE! | 0 | #VALUE! | 16 |  |  |  | module 51 |  | AirPd | UDF
167.6562 | 0 | #VALUE! | 0 | #VALUE! | 16
299.0625 | 10 | #VALUE! | #VALUE! | #VALUE! | 18
480.3125 | 10 | #VALUE! | #VALUE! | #VALUE! | 6
1450 | 14 | #VALUE! | #VALUE! | #VALUE! | 20